## Sheet1
Khối lượng khói sinh ra trong gian phòng
NFPA 92 - Phương trình (5.5.1.1e) - tính cho m
|  | = | Khối lượng dòng khói, kg/s
| Qc | = | Phần đối lưu của nhiệt phát sinh, kW
| z | = | Khoảng cách từ gốc ngọn lửa đến bề mặt lớp khói , (m)
| Cp | = | Nhiệt dung riêng của khối khí, (kJ/kgºC)
Khối lượng sản sinh khói
| Lượng nhiệt sinh ra từ đám cháy |  |  |  |  | : | Q | = | 4600 | kW
Tính cho vật liệu dễ cháy, nhiệt lượng 500 KW/m2, diện tích đám cháy tính toán 9,29 m2
| Phần đối lưu của nhiệt phát sinh Qc = 70% x Q |  |  |  |  | : | Qc | = | 3220 | kW
| Khoảng cách từ gốc ngọn lửa đến bề mặt lớp khói |  |  |  |  | : | z | = | 2.5 | m
| Nhiệt độ môi trường |  |  |  |  | : | To | = | 40 | ºC
| Nhiệt dung riêng của khối khí |  |  |  |  | : | Cp | = | 1 | kJ/kgºC
[8 empty] | = | 10.63 | kg/s
| Chiều cao ngọn lửa | [5 empty] | zl | = | 4.3 | m
NFPA 92 - Phương trình (5.5.1.1d)
| Nhiệt độ trung bình của khói | [5 empty] | Ts | = | 343 | ºC
|  |  |  | NFPA 92 - Phương trình (5.5.5) |  |  |  | = | 616 | ºK
Tỷ trọng hỗn hợp khí-khói
[5 empty] | Áp suất tuyệt đối | : | p | = | 101325 | Pa
[5 empty] | Nhiệt độ trung bình của khói | : | Ts | = | 616 | ºK
[5 empty] | Hằng số của khí | : | R | = | 287 | J/kgºK
|  |  |  | NFPA 92 - Phương trình (5.8b) |  |  | ρp | = | 0.57313 | kg/m3
| Lưu lượng khói tính toán | [6 empty] | = | 18.6 | m3/s
[9 empty] | 66960 | m3/h
𝑧_𝑙=0.166×𝑄_𝑐^(2∕5)
𝑚┴•
𝑚┴•=0.071𝑄_𝑐^(1∕3) 𝑧^(5∕3)+0.0018𝑄_𝑐
𝑇_𝑠=𝑇_𝑜+𝑄_𝑐/(𝑚┴• 𝐶_𝑝 )
𝜌_𝑝=𝑝/(𝑅𝑇_𝑝 )
𝑉┴•=(𝑚┴•)/𝜌_𝑝
𝑉┴•
𝑚┴•
Note on B9: The convective portion of the heat release rate, Qc, can be estimated as 70 % of the total heat release rate. NFPA 92B - Guide for Smoke Management Systems in Malls, Atria, and Large Areas - 2000 Edition Appendix A Explanatory Material - A.3.4